## Checklist
Generator Maintenance SOP checklist
SOP-MNT-007 ¦ Rev 1.0 ¦ Owner: Maintenance Manager
Completed by: |  |  | Date: |  |  | Shift:
Step | Task | Details | Owner | Done | Initials | Time | Notes
5.1 | Review the PM schedule and run hours | Technician checks the generator's PM schedule and current run hours in the CMMS to confirm which tasks are due this visit. | Maintenance Technician
5.2 | Perform the visual inspection | Technician inspects the generator enclosure, engine and fuel lines for leaks, corrosion, loose connections or physical damage. | Maintenance Technician
5.3 | Check engine oil and coolant levels | Technician checks engine oil and coolant against the manufacturer's specified levels and tops up or schedules an oil change if due. | Maintenance Technician
5.4 | Test the battery and charging system | Electrician load-tests the starting battery, checks terminal connections for corrosion, and confirms the battery charger is maintaining the correct float voltage. Warning: Treat battery terminals as energized; wear insulated gloves and avoid creating a short across the terminals. | Maintenance Electrician
5.5 | Check the block heater and starting circuits | Technician confirms the block heater is warming the engine to the specified temperature and checks starting circuit wiring for damage or loose connections. | Maintenance Technician
5.6 | Perform the no-load start test | Technician starts the generator and runs it unloaded for the specified time, checking oil pressure, coolant temperature and voltage output against normal ranges. Checkpoint: Generator reaches rated voltage and frequency within the manufacturer's specified start time. | Maintenance Technician
5.7 | Inspect the fuel system and quality | Technician checks the fuel tank level, inspects for water or contamination using the fuel test kit, and confirms fuel filters are within their service interval. | Maintenance Technician
5.8 | Test the transfer switch | Electrician simulates a utility power loss to confirm the transfer switch signals the generator to start and switches the load over within the expected time. Checkpoint: Transfer switch completes the changeover within the manufacturer's specified time during the simulated outage. | Maintenance Electrician
5.9 | Perform the periodic load bank test | Technician and electrician run the generator against a load bank at the interval specified in the PM schedule to confirm it can carry its rated capacity without wet-stacking or overheating. | Maintenance Manager
5.10 | Check exhaust and ventilation | Technician inspects the exhaust system for leaks or damage and confirms generator room or enclosure ventilation louvers are clear and functioning. | Maintenance Technician
5.11 | Record run hours and test results | Technician logs run hours, test readings, fuel level and any alarms or faults observed in the generator run log and the CMMS. | Maintenance Technician
5.12 | Address alarms and schedule annual service | Maintenance manager reviews any alarm or out-of-range reading, arranges corrective repair, and schedules the manufacturer-recommended annual service with a qualified technician. | Maintenance Manager
Supervisor sign-off: |  |  | Date:

## SOP
Generator Maintenance SOP
Standard operating procedure
Document no. | SOP-MNT-007
Revision | 1.0
Owner | Maintenance Manager
Effective date | September 15, 2026
Review cycle | Every 12 months
1. Purpose
To make sure standby generators start and carry load reliably when needed, by keeping fluids, batteries, fuel and controls maintained and tested on a regular schedule.
2. Scope
Applies to standby and backup generators used for emergency or backup power. Portable generators used for temporary equipment power are covered by a separate procedure.
Definitions
No-load test | Starting and running the generator without connecting it to the building or equipment load, to confirm it starts and runs correctly.
Load bank test | Running the generator against a controlled test load to confirm it can carry its rated capacity, since standby generators rarely see full load in normal operation.
Transfer switch | The device that automatically switches power supply between utility power and the generator during an outage.
Run hours | The cumulative hours a generator has operated, tracked to schedule service intervals.
3. Responsibilities
Maintenance Technician | Performs visual inspections, fluid checks and routine test runs, and logs results.
Maintenance Electrician | Tests the transfer switch, battery charging system and electrical connections.
Maintenance Manager | Reviews test results, schedules annual service and load bank testing, and approves corrective repairs.
Facility Manager | Coordinates test timing with building operations and is notified of any generator that fails a readiness test.
RACI matrix
Perform the routine visual inspection | Maintenance Technician: R/A ¦ Maintenance Electrician: I ¦ Maintenance Manager: I ¦ Facility Manager: -
Perform the no-load start test | Maintenance Technician: R/A ¦ Maintenance Electrician: C ¦ Maintenance Manager: I ¦ Facility Manager: I
Perform the load bank test | Maintenance Technician: R ¦ Maintenance Electrician: R ¦ Maintenance Manager: A ¦ Facility Manager: C
Test the transfer switch | Maintenance Technician: C ¦ Maintenance Electrician: R/A ¦ Maintenance Manager: I ¦ Facility Manager: C
Schedule annual service | Maintenance Technician: I ¦ Maintenance Electrician: I ¦ Maintenance Manager: R/A ¦ Facility Manager: C
4. Materials and PPE
Materials, tools and systems
Generator PM schedule and manufacturer service manual
Multimeter and battery load tester
Fuel quality test kit
Load bank test equipment or contracted load bank service
Generator run log
Spill containment supplies
Personal protective equipment
Safety glasses
Hearing protection
Insulated gloves for electrical checks
Fuel-resistant gloves when checking the fuel system
5. Procedure
5.1 Review the PM schedule and run hours | Technician checks the generator's PM schedule and current run hours in the CMMS to confirm which tasks are due this visit. Owner: Maintenance Technician
5.2 Perform the visual inspection | Technician inspects the generator enclosure, engine and fuel lines for leaks, corrosion, loose connections or physical damage. Owner: Maintenance Technician
5.3 Check engine oil and coolant levels | Technician checks engine oil and coolant against the manufacturer's specified levels and tops up or schedules an oil change if due. Owner: Maintenance Technician
5.4 Test the battery and charging system | Electrician load-tests the starting battery, checks terminal connections for corrosion, and confirms the battery charger is maintaining the correct float voltage. Owner: Maintenance Electrician Warning: Treat battery terminals as energized; wear insulated gloves and avoid creating a short across the terminals.
5.5 Check the block heater and starting circuits | Technician confirms the block heater is warming the engine to the specified temperature and checks starting circuit wiring for damage or loose connections. Owner: Maintenance Technician
5.6 Perform the no-load start test | Technician starts the generator and runs it unloaded for the specified time, checking oil pressure, coolant temperature and voltage output against normal ranges. Owner: Maintenance Technician Checkpoint: Generator reaches rated voltage and frequency within the manufacturer's specified start time.
5.7 Inspect the fuel system and quality | Technician checks the fuel tank level, inspects for water or contamination using the fuel test kit, and confirms fuel filters are within their service interval. Owner: Maintenance Technician
5.8 Test the transfer switch | Electrician simulates a utility power loss to confirm the transfer switch signals the generator to start and switches the load over within the expected time. Owner: Maintenance Electrician Checkpoint: Transfer switch completes the changeover within the manufacturer's specified time during the simulated outage.
5.9 Perform the periodic load bank test | Technician and electrician run the generator against a load bank at the interval specified in the PM schedule to confirm it can carry its rated capacity without wet-stacking or overheating. Owner: Maintenance Manager
5.10 Check exhaust and ventilation | Technician inspects the exhaust system for leaks or damage and confirms generator room or enclosure ventilation louvers are clear and functioning. Owner: Maintenance Technician
5.11 Record run hours and test results | Technician logs run hours, test readings, fuel level and any alarms or faults observed in the generator run log and the CMMS. Owner: Maintenance Technician
5.12 Address alarms and schedule annual service | Maintenance manager reviews any alarm or out-of-range reading, arranges corrective repair, and schedules the manufacturer-recommended annual service with a qualified technician. Owner: Maintenance Manager
6. Quality checks
No-load start tests are completed on the full PM schedule with no missed intervals.
Every load bank test result is compared against the generator's rated capacity.
Transfer switch changeover time is recorded and compared to the manufacturer's specification.
Fuel quality is tested at the scheduled interval and any contamination is addressed before the next outage.
7. Records
Generator run log with test results
Load bank test reports
Transfer switch test results
Annual service records
8. KPIs
Percentage of scheduled test runs completed
Generator failures to start on demand
Load bank test pass rate
Average transfer switch changeover time
9. Common mistakes
Only performing no-load tests and never load bank testing the generator.
Letting the battery charger go unchecked until the battery fails to start the engine.
Skipping fuel quality checks on generators that run infrequently.
Not recording run hours accurately, causing missed service intervals.
Assuming a successful no-load test means the generator can carry full building load.
10. Revision history
1.0 | Date: September 15, 2026 ¦ Description: Initial release ¦ Reviewed by: Ilia Pirozhenko

## Training Log
Generator Maintenance SOP training log
Record every employee trained on this SOP.
Employee name | Role | Date trained | Trainer | Employee signature | Trainer signature | Notes

## Revision Log
Generator Maintenance SOP revision log
Revision | Date | Description | Changed by | Approved by
1.0 | September 15, 2026 | Initial release | Ilia Pirozhenko

## About
About this template
This checklist comes from the free SOP template library by Perfect Wiki.
Open the template page
Keep this SOP up to date where your team works
Add it to Perfect Wiki so your team can find it and ask questions about it in Microsoft Teams, Slack, kChat or Mattermost.
Add to Perfect Wiki
This is a template. Adapt it to your organization, equipment and local regulations before use.